Ranking by Users: ESS = Essential; DES = Desirable; No rank = No opinion

S = SCR T = TCR O = OPAL D = DELPHI A = ALEPH L = L3

Comment: User requirements given and discussed in the AL3S meetings up to meeting #6, are marked with abbreviations as defined under #2. Those given after 9th June, 1998 are marked with the full name.

Abbreviations: SCR = Safety-Control-Room (TIS/FB); TCR = Technical-Control-Room (ST/MC); MCR = Meyrin-Control-Room (PS-Complex); PCR = Prévessin-Control-Room (SPS/LEP); X = Experiment; XCR = Experiment-Control-Room; SLIMOS = Section-Leader-In-Matters-Of-Safety; GLIMOS = Group-Leader-In-Matters-Of-Safety AS = Alarm-System; AL3 = Alarm-Level-3; AL3S = Alarm-Level-3-System; AL2 = Alarm-Level-2; CAS = Central-Alarm-Server; IS # = Safety-Instruction # (TIS); AFM = Auxiliary-Fire-Man UPS = Uninterrupted Power Supply; EPROM = Erasable-Programmable-Read-Only-Memory; ANS = Alarm-Notification-System; GSM = Global-System-Mobile (portable telephone); VESDA = Very Early Smoke Detection Apparatus

|  | Responsibilities | ESS | DES |
| --- | --- | --- | --- |
|  | Responsibility for the entire AL3S must be with one single CERN entity (avoid dilution of responsibility) | STDAL | O |
|  | Sensors | OL | D |
|  | Alarm transmission | ODL |  |
|  | Local and SCR synoptic | L | OD |
|  | Delivery of software and hard-wired signal for X | L | OD |
|  | Maintenance | ODL |  |
|  | Responsibility if more than one CERN entity involved; S: why vacillate? |  |  |
|  | Clear definition of responsibility for the entire alarm chain | TODL |  |
|  | AL3S Coordinator required | TAL | OD |
|  | One technical responsible for AL3S per experiment (for both sides X and technical group) | SAL | OD |

|  | Sensors and Detectors | ESS | DES |
| --- | --- | --- | --- |
|  | Who defines the type of sensors? O: ST, but large experiments need to be consulted for environmental reasons |  |  |
|  | Need uniformity for all experiments | SDL | TOA |
|  | Smoke/fire sensors can be uniform; "VESDA" is not liked by some specialists, but works really well | DL | O |
|  | Gas leak sensors probably uniform as well | DL | O |
|  | Does CERN need to have a study done for the choice of sensors? O: not necessarily | DL |  |
|  | Is there enough competence at CERN or do we need to call for the collaboration of outside specialists? |  | ODL |
|  | Any new type of sensor must be tested for at least one year under realistic conditions before it can be accepted; O: not necessarily | DL |  |
|  | Intelligent sensors? O: if exists and cost OK |  | DL |
|  | X need sensitive detectors for early detection | SO |  |
|  | Sniffing tubes "SDN" right inside the detectors | ODL |  |
|  | Best/right detector correctly placed | SOL | TD |
|  | Adapted to environment | SOL |  |
|  | Gas leak detectors with read-out for drift analysis | TL | XDA |
|  | Reduce false alarms due to detector drifts | STAL | OD |
|  | Minimum drift; calibration no more than every three months; O: 3-6 months (even longer; aim for 12 months, ie. at long shut-down) | TL | D |
|  | Every single detector should create AL3, no combination "2 of 2" which creates delay, decreases sensitivity and degree of safety; (however, some X are happy with "2 of 2"). S: this must be clarified | D | OL |

|  | Detection System | ESS | DES |
| --- | --- | --- | --- |
|  | Flexibility required | ODAL |  |
|  | Nobody will be able to foresee everything at the beginning of LHC; O: true | OD | L |
|  | Upgrading | TL | D |
|  | Possibility for change to new technology equipment; O: cost | STDL | A |
|  | Possibility for adding new alarms; O: always needed | STODAL |  |
|  | Changeable (no EPROM); O: don't understand. | T | DL |
|  | Possibility to change AL3 to AL2 and vice versa; O: not obvious; (needs to be better defined; modification in 1d, in 6m?) | TL | D |
|  | Maintenance | DL |  |
|  | Possibility for adding/changing actions | ODL | A |
|  | Additions, relocation | L | D |
|  | Information on system state required | OD |  |
|  | Information on state (fault) for X Slow Controls | L | OD |
|  | Provide all alarm levels, not only AL3; O: all alarm levels should be available but will not necessarily be needed | AL | OD |
|  | Information on signal level required | T | D |
|  | Analogue signals for SCR, TCR, XCR to monitor environment (smoke, fire, gas) and evolution | TD | OAL |
|  | Give global picture of alarm situation | ODL |  |
|  | Can be via fieldbus or by additional outputs; O: yes | L | OD |

|  | Alarm System | ESS | DES |
| --- | --- | --- | --- |
|  | Independence | S | D |
|  | Independent from Slow Control System | OA | DL |
|  | Independent from Data Acquisition System | OAL | D |
|  | Dedicated server for AL3S | ODL |  |
|  | Efficient database to manage AL3 | Tyrrell |  |
|  | Integrate "FB Intervention Report" with AL3S and DB | Tyrrell / S |  |
|  | Reduce False Alarms | TD |  |
|  | Reduce false alarms due to inappropriate detector type | STODAL |  |
|  | Reduce false alarms due to inappropriate placement of sensor | STOAL | D |
|  | Reduce false alarms due to drift of sensors | STOAL | D |
|  | Motivated false alarms (smoking) are acceptable; O: yes | O | TDAL |

|  | Alarm Transmission System | ESS | DES |
| --- | --- | --- | --- |
|  | Consider two separate, totally independent ( hot redundancy) , identical informatic systems instead of a hardware and a software one | Benincasa |  |
|  | Fail safe transmission required | STODAL |  |
|  | Surveillance of transmission | STOL | D |
|  | Power supply, short-circuit, cable interruption | SOL | D |
|  | The entire chain and all components must obey "fail-safe" | STXAL | D |
|  | Thorough testing on site that "fail-safe" is really met | STOAL | D |
|  | Hard-wired transmission | SDL |  |
|  | Need more information via hard-wired channel | L | SD |
|  | Location and type of alarm (currently eight: fire, gas leak, emergency stop, etc) | L | SOD |
|  | It must be possible to acknowledge or to isolate alarms in order to free the transmission line between local and SCR panel for other alarms | STOAL | D |
|  | Reliability | SDL |  |
|  | Improve reliability of informatic transmission system | SL | ODA |
|  | Reduce number of false alarms | STDL | O |
|  | No false alarms caused by informatic system | TDAL | S |
|  | Provide two-way communication with lifts O: there is a phone inside each LEP lift. Essential for such deep pits | SOL | TD |
|  | It is essential that the back-up transmission system should enable the fire brigade to make a response identical to that achievable with the primary system. This means that full alarm level 3 information, which includes exact location of the detector on alarm and its type, must be available through both the primary and back-up transmission routes. | Gilbert |  |

|  | Synoptic of local zone | ESS | DES |
| --- | --- | --- | --- |
|  | Useable for SLIMOS | O | DL |
|  | Location, access and information adapted for use by SLIMOS. Problem for some points, as distance XC - SY 250 m. | OL | D |
|  | High turn around and short training period of SLIMOS. O: CERN will never have enough staff to run professional SLIMOS. Thus we are stuck with the use of many SLIMOS for relatively short periods of duty. |  | L |
|  | Provide specific AL3 training for SLIMOS | OL | TD |
|  | Place local synoptic panel always in SY building; O: I have no opinion on this. A: no, not accessible for SLIMOS, SY locked!; S: give a key for the SY to the SLIMOS | ST | DL |
|  | The type and exact location of each "AL3" for a 'Safety-Zone' shall be displayed at a dedicated 'local-synoptic-panel', situated within the 'Safety Zone' concerned. | Gilbert |  |

|  | Destination of Alarms | ESS | DES |
| --- | --- | --- | --- |
|  | First destination of AL3 is SCR; O: best. | STODL |  |
|  | TCR (MCR, PCR possibly via TCR?) | TD | L |
|  | TCR to get all AL3 | STOD | L |
|  | TCR to get all AL1 and AL2 related to AL3S | STDL | O |
|  | TCR is emergency CR for TIS/FB in case SCR unavailable | STOL | D |
|  | All XCR for their system and their service environment; O: needed as they are in place | TOAL | D |
|  | Eg. XCR need to know state of electric circuit breakers | OAL | D |
|  | Inform other interested parties via ANS and GSM; O: needed when no shifts in XCR | O | DL |

|  | Alarm Display | ESS | DES |
| --- | --- | --- | --- |
|  | Audible Signal | SDL | O |
|  | Arriving alarms with audible signal; O: L2, L3 | TDAL | O |
|  | Operator's choice to enable or to disable | OD | TAL |
|  | Acknowledging alarm should stop audible signal | STAL | OD |
|  | Visual Signal | SDL |  |
|  | Use flashing light to signal new messages; S: flashing text | OXD | L |
|  | Operator's choice to enable or to disable |  | DAL |
|  | User-friendly Alarm Display Interface and Messages | STDL |  |
|  | Need clear set of definitions linking "detector", "alarm descriptions", "led definitions on local synoptic panel" "alarm general related to local synoptic panel", "data sheets and tests" | Tyrrell |  |
|  | Define messages in close collaboration with users (Fire Brigade); A: and GLIMOS | STDL | OA |
|  | Alarm texts for AL3 to be defined by Fire Brigade | SL | TD |
|  | Alarm message should identify "zone" | SODL | T |
|  | Alarm message always to identify exact address (room, gallery, tunnel sector) | SDAL | O |
|  | Unique identification of Red Phone (not line number for cluster of Red Phones) | SL | OD |
|  | Avoid flood of alarms (use filter for alarm reduction) | TDL | O |
|  | Group AL2s belonging to AL3 sub-systems | TL | ODA |
|  | Always signal new alarm in a group which is already acknowledged | TOL | DA |
|  | Provide access to historic data in grouped alarms | TOL | DA |
|  | Keep information to what is necessary | TOD |  |
|  | SLIMOS has many tasks, and is flooded with information, including Slow Controls | DL |  |
|  | Do not display field without interest for the end-user (SLIMOS) A: who decides? | DL |  |
|  | There are presently too many "headers" without utility for the user | DL |  |
|  | Alarm Messages must be clear and intelligible for the intended user | STODL |  |
|  | Language of messages (only English, not bilingual) | D | SAL |
|  | Uniform syntax of all messages | TSL | D |
|  | Not enough to suggest uniform syntax, must propose the syntax in agreement with the end-user | Benincasa |  |
|  | Use "clear full text", not abbreviations | AL | SD |
|  | Create and use standardised glossary (vocabulary) | ST | DL |
|  | Can pictograms be used? O: why not? |  | DL |
|  | Modification of data, text and alarm-help data "real-time" | TL | D |
|  | Presently CAS update once per month; change only effective after update |  | D |
|  | High turnover of XCR operators with short training period |  | D |
|  | AL3 to be integrated by X Controls in XCR's AS¸O: but passively | OAL | D |
|  | Possibility to direct alarms to separate screens | T | ODL |
|  | Alarms from system tests on "test" screen | STA | ODL |
|  | Alarms due to maintenance on "maintenance" screen | STA | ODL |
|  | Good information available in the two transmission systems shall not be degraded to suit an existing reception system. Full AL3S information shall be received in the SCR by either transmission route, as needed by the Fire Brigade for efficient and rapid intervention. | Gilbert |  |
|  | An overview summary of the 'Safety-Zones' on alarm in the two transmission channels shall be displayed at a dedicated 'central-synoptic-panel' in the alarm-receiving centre. An identical redundant panel shall be installed at the technical monitoring centre. The panels shall be in the form of a map of all CERN sites, accurately to a large scale, with correct juxtaposition, showing all intervening territory, with "North-up" orientation. | Gilbert |  |

|  | Control Rooms SCR and TCR | ESS | DES |
| --- | --- | --- | --- |
|  | Synoptic displays | DL |  |
|  | Simple access to synoptic displays | STODL |  |
|  | Simple navigation through synoptic displays | STODL |  |
|  | Improve information on synoptic displays | TL | SD |
|  | Accurate geographical location of all AL3 | STODL |  |
|  | Indication of % smoke obscuration for all underground and surface buildings) | STL | D |
|  | Use 2D as well as 3D plans | S | TDL |
|  | Show location and status of automatic extinguishing systems | SL | TD |
|  | Show location of detection and local synoptic panels | SOL | TD |
|  | Provide historic data in synoptic (replay) | STO | DL |
|  | Provide remote actions for AL2 (faults) of AL3S for TCR | T | ODL |
|  | More facilities in SCR | L | D |
|  | Print of text and graphical display of location; S: text at least | SDL |  |
|  | Access to video surveillance images; O: when available | SL | OD |
|  | More underground video surveillance | SL | D |
|  | Consider latest development in control room ergonomics | ST | DL |
|  | The back-up system currently operating requires a journey to the local zone synoptic to retrieve the exact address and type of alarm. This is not acceptable in the future. The full AL3 information shall be available on a dedicated ' back-up human interface' in the SCR. | Gilbert |  |
|  | The AL3 information shall be received in the SCR in three ways : 1)Human computer interface, linked to the primary transmission channel, giving full AL3 information plus all other available information (graphic displays, smoke concentration, etc.) by navigation. 2) Back-up Human interface, linked to the back-up transmission channel, independent of 1, above, giving full AL3 information of type and exact address of detector head on alarm. 3)Wall display giving overview of safety zones on alarm and possibly faults. | Gilbert |  |

|  | Distribution, Logging and Retrieval of Alarm Data | ESS | DES |
| --- | --- | --- | --- |
|  | Data in general |  |  |
|  | A Data-Exchange-Interface must be defined | Tejessy |  |
|  | All data should in principle be available X picks up what is of interest to them | D AL | TOD |
|  | Data available also for all surrounding services | L | TODA |
|  | Logging of Alarms | STDA |  |
|  | Permit post-mortem analysis of events | TODAL |  |
|  | Module for statistical evaluation and graphical representation of alarms | Jansson |  |
|  | XCR must have access to logged alarms | TAL | D |
|  | X want to log AL3 themselves; Logging of AL3 is part of the task of the X Slow controls; A: but do not rely on X slow Controls for logging | ODA | L |

|  | Effects of AL3 on Experiments | ESS | DES |
| --- | --- | --- | --- |
|  | AL3 and automatic actions | D |  |
|  | A maximum of thought to be given for automatic actions | SODAL |  |
|  | Relief SLIMOS, reduce human errors | ODL |  |
|  | Eg. after gas-leak detection: close gas supply valves, shut off HV; A: Delay? | ODL |  |
|  | Automatic actions via hard contacts, not software | DL | O |
|  | Use output contact from PLC |  | DL |
|  | If we use only informatic systems, the computer(s) check appropriate parameters (procedure to be decided by specialist case by case), in order to decide if it is a false or a true alarm. Following this investigation the computer can decide if the concerned part of the experiment must be switched off or not. | Benincasa |  |
|  | Minimise adverse effects of AL3 | TAL | OD |
|  | Minimise down-time after AL3 | TDAL | O |
|  | Provide remote reset of AL3; S: to avoid cutting beam unnecessarily; O: could be useful in certain cases | STAL | D |
|  | As far as Safety Rules permit | STAL | OD |
|  | Availability of more information (analogue values) will help | TL | DA |
|  | Improve relations between users and service providers | TDAL |  |

|  | Electric Power Supply System | ESS | DES |
| --- | --- | --- | --- |
|  | UPS | SDAL |  |
|  | Number of UPS dispersed around LEP causes concern |  | DL |
|  | Emergency Stop cuts inlet but not outlet of UPS (?) See also IS 5 & IS 40 O: we have modified all so that local emergency stop cuts both inlet and outlet. Automatic actions just cut input. A: needed as power cut too brutal; means control system on UPS for safe run-down. |  | D |

|  | Installation | ESS | DES |
| --- | --- | --- | --- |
|  | Prevent interference | STL | D |
|  | Installation of cables to prevent interference from lightening | L | TD |
|  | Prevent other electrical interference | L | TOD |
|  | Location of detection panel |  |  |
|  | For surface buildings always in SY building; A: NO! No SLIMOS access, SY locked!; : give a key for the SY to the SLIMOS | ST | DL |
|  | For underground areas at each level served by lift | AL | XTD |
|  | All detection panels accessible without beam stop | STOAL | D |

|  | Testing | ESS | DES |
| --- | --- | --- | --- |
|  | Device realistic tests for AL3S | STDL |  |
|  | Realistic test for gas-leak and automatic actions | STODL |  |
|  | Functional testing = Signal Transmission | STODAL |  |
|  | bypass "key" to avoid unwanted strong actions on equipment | TOA | DL |
|  | Afterwards, make sure bypass "key" is not forgotten | TOAL | D |
|  | use informatics system for that and not humans | OL | D |

|  | Operation | ESS | DES |
| --- | --- | --- | --- |
|  | Documentation | STD |  |
|  | Provide up-to-date simple and clear documentation for TCR operators on site | TODAL |  |
|  | Provide all documentation ONLINE | Jansson |  |
|  | Provide more and better technical training for TCR operators for better judgement of safety and risk matters | TDL |  |
|  | Instructions for AL3 | TD |  |
|  | Provide instructions for all Control Rooms for procedures and collaboration with Fire Brigade | STOAL | D |
|  | Train operators and SLIMOS for collaboration with Fire Brigade in emergency situations; O: but difficult if many SLIMOSs. | STAL | OD |
|  | Provide Training package with documentation and slides for ONLINE TRAINING | Jansson |  |

|  | Maintenance | ESS | DES |
| --- | --- | --- | --- |
|  | Maintenance of AL3S for LHC only during limited access | TDL |  |
|  | IS 37 using electronic procedure via EDH | Jansson |  |
|  | Maintenance must be authorised ahead by GLIMOS | TODAL |  |
|  | See also new IS 37 |  |  |
|  | Inform SLIMOS of any action on the detection system | DA | T |
|  | Before any maintenance work | ODAL |  |
|  | Before any adjustment | DAL |  |
|  | By "automatic" signalling of ongoing maintenance | DAL |  |
|  | Announce also when finished before leaving the area | DAL | O |
|  | Inform if intervention successful; O: if unsuccessful. | ODAL |  |
|  | Contract firms have to stick to these rules as well | ODAL |  |
|  | Provide mode "maintenance" to inhibit false alarms | STA | D |
|  | Make "inhibit" signal available for XCR and TCR | TODAL |  |
|  | "Inhibit" for zone? For central? For detector/sensor? | TL | DL |
|  | Relation of "inhibit" with automatic action? O: should block such actions. | TL | D |
|  | Inhibit AL3 and all AL1 and AL2 send to TCR; O: yes, during maintenance unless testing | T | DL |
|  | Make sure maintenance inhibit is not forgotten once maintenance finished | STODAL |  |

|  | Procedures | ESS | DES |
| --- | --- | --- | --- |
|  | Procedures/Rules must be adapted to be in line with evolution of installation, of technology | STOL | D |
|  | Procedures/Rules/Regulations one collection and also ONLINE | Jansson |  |
|  | Clear Instructions of Actions | TDAL |  |
|  | Short instruction (one page max) | TOL | DA |
|  | Clear instructions for actions in case of AL3; (WHO does WHAT) | STODAL |  |
|  | Safety instructions say "Wait for FB"; that is not reasonable, SLIMOS and others need to act whilst FB on its way; S: those who act must be trained and equipped | ODA | L |
|  | Auxiliary Fireman (AFM) | SL | D |
|  | Does INB require AFM on site? O: LHC one may do. LEP is ambiguous; A: 24h/d, each X, based in XCR | L | D |
|  | If so, need to be trained and equipped | SOL | D |
|  | If so, AL3 must be send via ANS to GSM of AFM | OL | D |
|  | Access forbidden to pit at AL3; A: !! (see line # 211 before "Wait for FB") | D |  |
|  | Flashing light after Fire detection to forbid access? A: ! | ODL |  |
|  | Unclear procedure for SLIMOS and Auxiliary Fireman on what to do; A: !! | DL |  |
|  | Evacuation at AL3 "Fire"; presently unclear procedure; O: true; A: !! | OD | L |
|  | Visitors and AL3 |  |  |
|  | To be clarified who is responsible for visitors (not GLIMOS!) that person must be competent and trained; O:this needs to be discussed with LHC experiments on this. LEP is almost sorted out after 10 y of visits. | ODAL |  |